## 32xxx
Input Registers 32XXX
No. | Input Register | Name | Data Type | Address Group | Floor
1 | 32001 | Status Control AC1 | 16 bit binnary | 1.00 | 1
2 | 32002 | Status Control AC2 | 16 bit binnary
3 | 32003 | Temperature Set Point | 16 bit signed integer
4 | 32004 | - | -
5 | 32005 | Room Temperature | 16 bit signed integer
6 | 32006 | -
7 | 32007 | Status Control AC1 | 16 bit binnary | 1.01
8 | 32008 | Status Control AC2 | 16 bit binnary
9 | 32009 | Temperature Set Point | 16 bit signed integer
10 | 32010 | - | -
11 | 32011 | Room Temperature | 16 bit signed integer
12 | 32012 | -
13 | 32013 | Status Control AC1 | 16 bit binnary | 1.02 | 2
14 | 32014 | Status Control AC2 | 16 bit binnary
15 | 32015 | Temperature Set Point | 16 bit signed integer
16 | 32016 | - | -
17 | 32017 | Room Temperature | 16 bit signed integer
18 | 32018 | -
19 | 32019 | Status Control AC1 | 16 bit binnary | 1.03
20 | 32020 | Status Control AC2 | 16 bit binnary
21 | 32021 | Temperature Set Point | 16 bit signed integer
22 | 32022 | - | -
23 | 32023 | Room Temperature | 16 bit signed integer
24 | 32024 | -
25 | 32025 | Status Control AC1 | 16 bit binnary | 1.04
26 | 32026 | Status Control AC2 | 16 bit binnary
27 | 32027 | Temperature Set Point | 16 bit signed integer
28 | 32028 | - | -
29 | 32029 | Room Temperature | 16 bit signed integer
30 | 32030 | -
31 | 32031 | Status Control AC1 | 16 bit binnary | 1.05
32 | 32032 | Status Control AC2 | 16 bit binnary
33 | 32033 | Temperature Set Point | 16 bit signed integer
34 | 32034 | - | -
35 | 32035 | Room Temperature | 16 bit signed integer
36 | 32036 | -
37 | 32037 | Status Control AC1 | 16 bit binnary | 1.06
38 | 32038 | Status Control AC2 | 16 bit binnary
39 | 32039 | Temperature Set Point | 16 bit signed integer
40 | 32040 | - | -
41 | 32041 | Room Temperature | 16 bit signed integer
42 | 32042 | -
43 | 32043 | Status Control AC1 | 16 bit binnary | 1.07
44 | 32044 | Status Control AC2 | 16 bit binnary
45 | 32045 | Temperature Set Point | 16 bit signed integer
46 | 32046 | - | -
47 | 32047 | Room Temperature | 16 bit signed integer
48 | 32048 | -
49 | 32049 | Status Control AC1 | 16 bit binnary | 1.08
50 | 32050 | Status Control AC2 | 16 bit binnary
51 | 32051 | Temperature Set Point | 16 bit signed integer
52 | 32052 | - | -
53 | 32053 | Room Temperature | 16 bit signed integer
54 | 32054 | -
55 | 32055 | Status Control AC1 | 16 bit binnary | 1.09 | 3
56 | 32056 | Status Control AC2 | 16 bit binnary
57 | 32057 | Temperature Set Point | 16 bit signed integer
58 | 32058 | - | -
59 | 32059 | Room Temperature | 16 bit signed integer
60 | 32060 | -
61 | 32061 | Status Control AC1 | 16 bit binnary | 1.1
62 | 32062 | Status Control AC2 | 16 bit binnary
63 | 32063 | Temperature Set Point | 16 bit signed integer
64 | 32064 | - | -
65 | 32065 | Room Temperature | 16 bit signed integer
66 | 32066 | -
67 | 32067 | Status Control AC1 | 16 bit binnary | 1.11
68 | 32068 | Status Control AC2 | 16 bit binnary
69 | 32069 | Temperature Set Point | 16 bit signed integer
70 | 32070 | - | -
71 | 32071 | Room Temperature | 16 bit signed integer
72 | 32072 | -
73 | 32073 | Status Control AC1 | 16 bit binnary | 1.12
74 | 32074 | Status Control AC2 | 16 bit binnary
75 | 32075 | Temperature Set Point | 16 bit signed integer
76 | 32076 | - | -
77 | 32077 | Room Temperature | 16 bit signed integer
78 | 32078 | -
79 | 32079 | Status Control AC1 | 16 bit binnary | 1.13
80 | 32080 | Status Control AC2 | 16 bit binnary
81 | 32081 | Temperature Set Point | 16 bit signed integer
82 | 32082 | - | -
83 | 32083 | Room Temperature | 16 bit signed integer
84 | 32084 | -
85 | 32085 | Status Control AC1 | 16 bit binnary | 1.14
86 | 32086 | Status Control AC2 | 16 bit binnary
87 | 32087 | Temperature Set Point | 16 bit signed integer
88 | 32088 | - | -
89 | 32089 | Room Temperature | 16 bit signed integer
90 | 32090 | -
91 | 32091 | Status Control AC1 | 16 bit binnary | 1.15
92 | 32092 | Status Control AC2 | 16 bit binnary
93 | 32093 | Temperature Set Point | 16 bit signed integer
94 | 32094 | - | -
95 | 32095 | Room Temperature | 16 bit signed integer
96 | 32096 | -
97 | 32097 | Status Control AC1 | 16 bit binnary | 2
98 | 32098 | Status Control AC2 | 16 bit binnary
99 | 32099 | Temperature Set Point | 16 bit signed integer
100 | 32100 | - | -
101 | 32101 | Room Temperature | 16 bit signed integer
102 | 32102 | -
103 | 32103 | Status Control AC1 | 16 bit binnary | 2.01
104 | 32104 | Status Control AC2 | 16 bit binnary
105 | 32105 | Temperature Set Point | 16 bit signed integer
106 | 32106 | - | -
107 | 32107 | Room Temperature | 16 bit signed integer
108 | 32108 | -
109 | 32109 | Status Control AC1 | 16 bit binnary | 2.02
110 | 32110 | Status Control AC2 | 16 bit binnary
111 | 32111 | Temperature Set Point | 16 bit signed integer
112 | 32112 | - | -
113 | 32113 | Room Temperature | 16 bit signed integer
114 | 32114 | -
115 | 32115 | Status Control AC1 | 16 bit binnary | 2.03
116 | 32116 | Status Control AC2 | 16 bit binnary
117 | 32117 | Temperature Set Point | 16 bit signed integer
118 | 32118 | - | -
119 | 32119 | Room Temperature | 16 bit signed integer
120 | 32120 | -
121 | 32121 | Status Control AC1 | 16 bit binnary | 2.04
122 | 32122 | Status Control AC2 | 16 bit binnary
123 | 32123 | Temperature Set Point | 16 bit signed integer
124 | 32124 | - | -
125 | 32125 | Room Temperature | 16 bit signed integer
126 | 32126 | -
127 | 32127 | Status Control AC1 | 16 bit binnary | 2.05
128 | 32128 | Status Control AC2 | 16 bit binnary
129 | 32129 | Temperature Set Point | 16 bit signed integer
130 | 32130 | - | -
131 | 32131 | Room Temperature | 16 bit signed integer
132 | 32132 | -
133 | 32133 | Status Control AC1 | 16 bit binnary | 2.06 | 4
134 | 32134 | Status Control AC2 | 16 bit binnary
135 | 32135 | Temperature Set Point | 16 bit signed integer
136 | 32136 | - | -
137 | 32137 | Room Temperature | 16 bit signed integer
138 | 32138 | -
139 | 32139 | Status Control AC1 | 16 bit binnary | 2.07
140 | 32140 | Status Control AC2 | 16 bit binnary
141 | 32141 | Temperature Set Point | 16 bit signed integer
142 | 32142 | - | -
143 | 32143 | Room Temperature | 16 bit signed integer
144 | 32144 | -
145 | 32145 | Status Control AC1 | 16 bit binnary | 2.08
146 | 32146 | Status Control AC2 | 16 bit binnary
147 | 32147 | Temperature Set Point | 16 bit signed integer
148 | 32148 | - | -
149 | 32149 | Room Temperature | 16 bit signed integer
150 | 32150 | -
151 | 32151 | Status Control AC1 | 16 bit binnary | 2.09
152 | 32152 | Status Control AC2 | 16 bit binnary
153 | 32153 | Temperature Set Point | 16 bit signed integer
154 | 32154 | - | -
155 | 32155 | Room Temperature | 16 bit signed integer
156 | 32156 | -
157 | 32157 | Status Control AC1 | 16 bit binnary | 2.1
158 | 32158 | Status Control AC2 | 16 bit binnary
159 | 32159 | Temperature Set Point | 16 bit signed integer
160 | 32160 | - | -
161 | 32161 | Room Temperature | 16 bit signed integer
162 | 32162 | -
163 | 32163 | Status Control AC1 | 16 bit binnary | 2.11
164 | 32164 | Status Control AC2 | 16 bit binnary
165 | 32165 | Temperature Set Point | 16 bit signed integer
166 | 32166 | - | -
167 | 32167 | Room Temperature | 16 bit signed integer
168 | 32168 | -
169 | 32169 | Status Control AC1 | 16 bit binnary | 2.12
170 | 32170 | Status Control AC2 | 16 bit binnary
171 | 32171 | Temperature Set Point | 16 bit signed integer
172 | 32172 | - | -
173 | 32173 | Room Temperature | 16 bit signed integer
174 | 32174 | -
175 | 32175 | Status Control AC1 | 16 bit binnary | 2.13
176 | 32176 | Status Control AC2 | 16 bit binnary
177 | 32177 | Temperature Set Point | 16 bit signed integer
178 | 32178 | - | -
179 | 32179 | Room Temperature | 16 bit signed integer
180 | 32180 | -
181 | 32181 | Status Control AC1 | 16 bit binnary | 2.14
182 | 32182 | Status Control AC2 | 16 bit binnary
183 | 32183 | Temperature Set Point | 16 bit signed integer
184 | 32184 | - | -
185 | 32185 | Room Temperature | 16 bit signed integer
186 | 32186 | -
187 | 32187 | Status Control AC1 | 16 bit binnary | 2.15
188 | 32188 | Status Control AC2 | 16 bit binnary
189 | 32189 | Temperature Set Point | 16 bit signed integer
190 | 32190 | - | -
191 | 32191 | Room Temperature | 16 bit signed integer
192 | 32192 | -
193 | 32193 | Status Control AC1 | 16 bit binnary | 3
194 | 32194 | Status Control AC2 | 16 bit binnary
195 | 32195 | Temperature Set Point | 16 bit signed integer
196 | 32196 | - | -
197 | 32197 | Room Temperature | 16 bit signed integer
198 | 32198 | -
199 | 32199 | Status Control AC1 | 16 bit binnary | 3.01
200 | 32200 | Status Control AC2 | 16 bit binnary
201 | 32201 | Temperature Set Point | 16 bit signed integer
202 | 32202 | - | -
203 | 32203 | Room Temperature | 16 bit signed integer
204 | 32204 | -
205 | 32205 | Status Control AC1 | 16 bit binnary | 3.02 | 5
206 | 32206 | Status Control AC2 | 16 bit binnary
207 | 32207 | Temperature Set Point | 16 bit signed integer
208 | 32208 | - | -
209 | 32209 | Room Temperature | 16 bit signed integer
210 | 32210 | -
211 | 32211 | Status Control AC1 | 16 bit binnary | 3.03
212 | 32212 | Status Control AC2 | 16 bit binnary
213 | 32213 | Temperature Set Point | 16 bit signed integer
214 | 32214 | - | -
215 | 32215 | Room Temperature | 16 bit signed integer
216 | 32216 | -
217 | 32217 | Status Control AC1 | 16 bit binnary | 3.04
218 | 32218 | Status Control AC2 | 16 bit binnary
219 | 32219 | Temperature Set Point | 16 bit signed integer
220 | 32220 | - | -
221 | 32221 | Room Temperature | 16 bit signed integer
222 | 32222 | -
223 | 32223 | Status Control AC1 | 16 bit binnary | 3.05
224 | 32224 | Status Control AC2 | 16 bit binnary
225 | 32225 | Temperature Set Point | 16 bit signed integer
226 | 32226 | - | -
227 | 32227 | Room Temperature | 16 bit signed integer
228 | 32228 | -
229 | 32229 | Status Control AC1 | 16 bit binnary | 3.06
230 | 32230 | Status Control AC2 | 16 bit binnary
231 | 32231 | Temperature Set Point | 16 bit signed integer
232 | 32232 | - | -
233 | 32233 | Room Temperature | 16 bit signed integer
234 | 32234 | -
235 | 32235 | Status Control AC1 | 16 bit binnary | 3.07
236 | 32236 | Status Control AC2 | 16 bit binnary
237 | 32237 | Temperature Set Point | 16 bit signed integer
238 | 32238 | - | -
239 | 32239 | Room Temperature | 16 bit signed integer
240 | 32240 | -
241 | 32241 | Status Control AC1 | 16 bit binnary | 3.08
242 | 32242 | Status Control AC2 | 16 bit binnary
243 | 32243 | Temperature Set Point | 16 bit signed integer
244 | 32244 | - | -
245 | 32245 | Room Temperature | 16 bit signed integer
246 | 32246 | -
247 | 32247 | Status Control AC1 | 16 bit binnary | 3.09 | 6
248 | 32248 | Status Control AC2 | 16 bit binnary
249 | 32249 | Temperature Set Point | 16 bit signed integer
250 | 32250 | - | -
251 | 32251 | Room Temperature | 16 bit signed integer
252 | 32252 | -
253 | 32253 | Status Control AC1 | 16 bit binnary | 3.1
254 | 32254 | Status Control AC2 | 16 bit binnary
255 | 32255 | Temperature Set Point | 16 bit signed integer
256 | 32256 | - | -
257 | 32257 | Room Temperature | 16 bit signed integer
258 | 32258 | -
259 | 32259 | Status Control AC1 | 16 bit binnary | 3.11
260 | 32260 | Status Control AC2 | 16 bit binnary
261 | 32261 | Temperature Set Point | 16 bit signed integer
262 | 32262 | - | -
263 | 32263 | Room Temperature | 16 bit signed integer
264 | 32264 | -
265 | 32265 | Status Control AC1 | 16 bit binnary | 3.12
266 | 32266 | Status Control AC2 | 16 bit binnary
267 | 32267 | Temperature Set Point | 16 bit signed integer
268 | 32268 | - | -
269 | 32269 | Room Temperature | 16 bit signed integer
270 | 32270 | -
271 | 32271 | Status Control AC1 | 16 bit binnary | 3.13
272 | 32272 | Status Control AC2 | 16 bit binnary
273 | 32273 | Temperature Set Point | 16 bit signed integer
274 | 32274 | - | -
275 | 32275 | Room Temperature | 16 bit signed integer
276 | 32276 | -
277 | 32277 | Status Control AC1 | 16 bit binnary | 3.14
278 | 32278 | Status Control AC2 | 16 bit binnary
279 | 32279 | Temperature Set Point | 16 bit signed integer
280 | 32280 | - | -
281 | 32281 | Room Temperature | 16 bit signed integer
282 | 32282 | -
283 | 32283 | Status Control AC1 | 16 bit binnary | 3.15
284 | 32284 | Status Control AC2 | 16 bit binnary
285 | 32285 | Temperature Set Point | 16 bit signed integer
286 | 32286 | - | -
287 | 32287 | Room Temperature | 16 bit signed integer
288 | 32288 | -
289 | 32289 | Status Control AC1 | 16 bit binnary | 4
290 | 32290 | Status Control AC2 | 16 bit binnary
291 | 32291 | Temperature Set Point | 16 bit signed integer
292 | 32292 | - | -
293 | 32293 | Room Temperature | 16 bit signed integer
294 | 32294 | -
295 | 32295 | Status Control AC1 | 16 bit binnary | 4.01
296 | 32296 | Status Control AC2 | 16 bit binnary
297 | 32297 | Temperature Set Point | 16 bit signed integer
298 | 32298 | - | -
299 | 32299 | Room Temperature | 16 bit signed integer
300 | 32300 | - | -

## Status Control AC 1
Status Control AC 1
Floor | Room | DIII Group Address | Input Registers
1 | Receptionist | 1.00 | 32001 | Bit | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
| Receptionist | 1.01 | 32007 | Description | - | Fan Speed |  |  | - | Fan Direction |  |  | Thermo Status | Heater Status | Fan Status | - | Normal Operation | Forced Off status | - | on/off status
2 | Adm. Office | 1.02 | 32013
| International Relation | 1.03 | 32019 | Meaning | - | 0-7 (bin) |  |  | - | 0-7 (bin) |  |  | 0 = OFF | 0 = OFF | 0 = OFF | - | 0 = Off | 0 = None | - | 0 = OFF
| Classroom 2201 | 1.04 | 32025 | [9 empty] | 1 = ON | 1 = ON | 1 = ON |  | 1 = On (Norm) | 1 = Forced Off |  | 1 = ON
| Computer Lab. | 1.05 | 32031 | [13 empty] | 0 = On (Error)
| Library | 1.06 | 32037
| Library Adm. | 1.07 | 32043
| Head Office | 1.08 | 32049
3 | Server/Technician | 1.09 | 32055
| Corridor | 1.10 | 32061
| Working Space 3rd Floor | 1.11 | 32067
| Classroom 2302 | 1.12 | 32073
| Post-Graduate | 1.13 | 32079
| Classroom 2303 | 1.14 | 32085
| Meeting Room 3rd Floor | 1.15 | 32091
| CK4BC Office | 2.00 | 32097
| Gamification | 2.01 | 32103
| Staff Gym | 2.02 | 32109
| Staff Gym | 2.03 | 32115
| Karaoke | 2.04 | 32121
| Karaoke | 2.05 | 32127
4 | Corridor | 2.06 | 32133
| Corridor | 2.07 | 32139
| Classroom 2405 | 2.08 | 32145
| Classroom 2404 | 2.09 | 32151
| Neurobusiness | 2.10 | 32157
| Faculty Room 4th Floor | 2.11 | 32163
| Economic Room | 2.12 | 32169
| Meeting Room 4th Floor | 2.13 | 32175
| Lecturer Room 4th Floor | 2.14 | 32181
| The Greater Hub | 2.15 | 32187
| Classroom 2403 | 3.00 | 32193
| Archieve Room | 3.01 | 32199
5 | Corridor | 3.02 | 32205
| Logistic Room | 3.03 | 32211
| Logistic Room | 3.04 | 32217
| Classroom 2507 | 3.05 | 32223
| Lecturer Room 5th Floor | 3.06 | 32229
| Musholla | 3.07 | 32235
| Faculty Room 5th Floor | 3.08 | 32241
6 | Waiting Room Auditorium | 3.09 | 32247
| Auditorium | 3.10 | 32253
| Auditorium | 3.11 | 32259
| Corridor 6th Floor | 3.12 | 32265
| Meeting Room 6th Floor | 3.13 | 32271
| Lecturer Room 6th Floor | 3.14 | 32277
| Ciel Room | 3.15 | 32283
| Visiting Prof. | 4.00 | 32289
| Control Room Auditorium | 4.01 | 32295

## Status Control AC 2
Status Control AC 2
Floor | Room | DIII Group Address | Input Registers
1 | Receptionist | 1.00 | 32002 | Bit | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
| Receptionist | 1.01 | 32008 | Description | Cool/Heat Master |  | Hot Start Status | - | Operation Status |  |  |  | Filter Sign Status |  |  |  | Operation Mode Setting
2 | Adm. Office | 1.02 | 32014
| International Relation | 1.03 | 32020 | Meaning | 0 = Not decided |  | 0 = Off | - | 0 = Fan |  |  |  | 0 = Off |  |  |  | 0-7 (bin)
| Classroom 2201 | 1.04 | 32026 |  | 1 = slave |  | 1 =On |  | 1 = Heating |  |  |  | 1-15 = On
| Computer Lab. | 1.05 | 32032 |  | 2 = Master |  |  |  | 2 = Cooling
| Library | 1.06 | 32038
| Library Adm. | 1.07 | 32044
| Head Office | 1.08 | 32050
3 | Server/Technician | 1.09 | 32056
| Corridor | 1.10 | 32062
| Working Space 3rd Floor | 1.11 | 32068
| Classroom 2302 | 1.12 | 32074
| Post-Graduate | 1.13 | 32080
| Classroom 2303 | 1.14 | 32086
| Meeting Room 3rd Floor | 1.15 | 32092
| CK4BC Office | 2.00 | 32098
| Gamification | 2.01 | 32104
| Staff Gym | 2.02 | 32110
| Staff Gym | 2.03 | 32116
| Karaoke | 2.04 | 32122
| Karaoke | 2.05 | 32128
4 | Corridor | 2.06 | 32134
| Corridor | 2.07 | 32140
| Classroom 2405 | 2.08 | 32146
| Classroom 2404 | 2.09 | 32152
| Neurobusiness | 2.10 | 32158
| Faculty Room 4th Floor | 2.11 | 32164
| Economic Room | 2.12 | 32170
| Meeting Room 4th Floor | 2.13 | 32176
| Lecturer Room 4th Floor | 2.14 | 32182
| The Greater Hub | 2.15 | 32188
| Classroom 2403 | 3.00 | 32194
| Archieve Room | 3.01 | 32200
5 | Corridor | 3.02 | 32206
| Logistic Room | 3.03 | 32212
| Logistic Room | 3.04 | 32218
| Classroom 2507 | 3.05 | 32224
| Lecturer Room 5th Floor | 3.06 | 32230
| Musholla | 3.07 | 32236
| Faculty Room 5th Floor | 3.08 | 32242
6 | Waiting Room Auditorium | 3.09 | 32248
| Auditorium | 3.10 | 32254
| Auditorium | 3.11 | 32260
| Corridor 6th Floor | 3.12 | 32266
| Meeting Room 6th Floor | 3.13 | 32272
| Lecturer Room 6th Floor | 3.14 | 32278
| Ciel Room | 3.15 | 32284
| Visiting Prof. | 4.00 | 32290
| Control Room Auditorium | 4.01 | 32296

## Temp SetPoint
Room Temperature Set Point
Floor | Room | DIII Group Address | Input Registers
1 | Receptionist | 1.00 | 32003
| Receptionist | 1.01 | 32009
2 | Adm. Office | 1.02 | 32015
| International Relation | 1.03 | 32021
| Classroom 2201 | 1.04 | 32027
| Computer Lab. | 1.05 | 32033
| Library | 1.06 | 32039
| Library Adm. | 1.07 | 32045
| Head Office | 1.08 | 32051
3 | Server/Technician | 1.09 | 32057
| Corridor | 1.10 | 32063
| Working Space 3rd Floor | 1.11 | 32069
| Classroom 2302 | 1.12 | 32075
| Post-Graduate | 1.13 | 32081
| Classroom 2303 | 1.14 | 32087
| Meeting Room 3rd Floor | 1.15 | 32093
| CK4BC Office | 2.00 | 32099
| Gamification | 2.01 | 32105
| Staff Gym | 2.02 | 32111
| Staff Gym | 2.03 | 32117
| Karaoke | 2.04 | 32123
| Karaoke | 2.05 | 32129
4 | Corridor | 2.06 | 32135
| Corridor | 2.07 | 32141
| Classroom 2405 | 2.08 | 32147
| Classroom 2404 | 2.09 | 32153
| Neurobusiness | 2.10 | 32159
| Faculty Room 4th Floor | 2.11 | 32165
| Economic Room | 2.12 | 32171
| Meeting Room 4th Floor | 2.13 | 32177
| Lecturer Room 4th Floor | 2.14 | 32183
| The Greater Hub | 2.15 | 32189
| Classroom 2403 | 3.00 | 32195
| Archieve Room | 3.01 | 32201
5 | Corridor | 3.02 | 32207
| Logistic Room | 3.03 | 32213
| Logistic Room | 3.04 | 32219
| Classroom 2507 | 3.05 | 32225
| Lecturer Room 5th Floor | 3.06 | 32231
| Musholla | 3.07 | 32237
| Faculty Room 5th Floor | 3.08 | 32243
6 | Waiting Room Auditorium | 3.09 | 32249
| Auditorium | 3.10 | 32255
| Auditorium | 3.11 | 32261
| Corridor 6th Floor | 3.12 | 32267
| Meeting Room 6th Floor | 3.13 | 32273
| Lecturer Room 6th Floor | 3.14 | 32279
| Ciel Room | 3.15 | 32285
| Visiting Prof. | 4.00 | 32291
| Control Room Auditorium | 4.01 | 32297

## Temp Room
Room Temperature
Floor | Room | DIII Group Address | Input Registers
1 | Receptionist | 1.00 | 32005
| Receptionist | 1.01 | 32011
2 | Adm. Office | 1.02 | 32017
| International Relation | 1.03 | 32023
| Classroom 2201 | 1.04 | 32029
| Computer Lab. | 1.05 | 32035
| Library | 1.06 | 32041
| Library Adm. | 1.07 | 32047
| Head Office | 1.08 | 32053
3 | Server/Technician | 1.09 | 32059
| Corridor | 1.10 | 32065
| Working Space 3rd Floor | 1.11 | 32071
| Classroom 2302 | 1.12 | 32077
| Post-Graduate | 1.13 | 32083
| Classroom 2303 | 1.14 | 32089
| Meeting Room 3rd Floor | 1.15 | 32095
| CK4BC Office | 2.00 | 32101
| Gamification | 2.01 | 32107
| Staff Gym | 2.02 | 32113
| Staff Gym | 2.03 | 32119
| Karaoke | 2.04 | 32125
| Karaoke | 2.05 | 32131
4 | Corridor | 2.06 | 32137
| Corridor | 2.07 | 32143
| Classroom 2405 | 2.08 | 32149
| Classroom 2404 | 2.09 | 32155
| Neurobusiness | 2.10 | 32161
| Faculty Room 4th Floor | 2.11 | 32167
| Economic Room | 2.12 | 32173
| Meeting Room 4th Floor | 2.13 | 32179
| Lecturer Room 4th Floor | 2.14 | 32185
| The Greater Hub | 2.15 | 32191
| Classroom 2403 | 3.00 | 32197
| Archieve Room | 3.01 | 32203
5 | Corridor | 3.02 | 32209
| Logistic Room | 3.03 | 32215
| Logistic Room | 3.04 | 32221
| Classroom 2507 | 3.05 | 32227
| Lecturer Room 5th Floor | 3.06 | 32233
| Musholla | 3.07 | 32239
| Faculty Room 5th Floor | 3.08 | 32245
6 | Waiting Room Auditorium | 3.09 | 32251
| Auditorium | 3.10 | 32257
| Auditorium | 3.11 | 32263
| Corridor 6th Floor | 3.12 | 32269
| Meeting Room 6th Floor | 3.13 | 32275
| Lecturer Room 6th Floor | 3.14 | 32281
| Ciel Room | 3.15 | 32287
| Visiting Prof. | 4.00 | 32293
| Control Room Auditorium | 4.01 | 32299

## Temp SetPoint Range
Room Temperature Set Point Range
Floor | Room | DIII Group Address | Input Registers (Cooling) | Input Registers (Heating)
1 | Receptionist | 1.00 | 31002 | 31003
| Receptionist | 1.01 | 31005 | 31006
2 | Adm. Office | 1.02 | 31008 | 31009
| International Relation | 1.03 | 31011 | 31012
| Classroom 2201 | 1.04 | 31014 | 31015
| Computer Lab. | 1.05 | 31017 | 31018
| Library | 1.06 | 31020 | 31021
| Library Adm. | 1.07 | 31023 | 31024
| Head Office | 1.08 | 31026 | 31027
3 | Server/Technician | 1.09 | 31029 | 31030
| Corridor | 1.10 | 31032 | 31033
| Working Space 3rd Floor | 1.11 | 31035 | 31036
| Classroom 2302 | 1.12 | 31038 | 31039
| Post-Graduate | 1.13 | 31041 | 31042
| Classroom 2303 | 1.14 | 31044 | 31045
| Meeting Room 3rd Floor | 1.15 | 31047 | 31048
| CK4BC Office | 2.00 | 31050 | 31051
| Gamification | 2.01 | 31053 | 31054
| Staff Gym | 2.02 | 31056 | 31057
| Staff Gym | 2.03 | 31059 | 31060
| Karaoke | 2.04 | 31062 | 31063
| Karaoke | 2.05 | 31065 | 31066
4 | Corridor | 2.06 | 31068 | 31069
| Corridor | 2.07 | 31071 | 31072
| Classroom 2405 | 2.08 | 31074 | 31075
| Classroom 2404 | 2.09 | 31077 | 31078
| Neurobusiness | 2.10 | 31080 | 31081
| Faculty Room 4th Floor | 2.11 | 31083 | 31084
| Economic Room | 2.12 | 31086 | 31087
| Meeting Room 4th Floor | 2.13 | 31089 | 31090
| Lecturer Room 4th Floor | 2.14 | 31092 | 31093
| The Greater Hub | 2.15 | 31095 | 31096
| Classroom 2403 | 3.00 | 31098 | 31099
| Archieve Room | 3.01 | 31101 | 31102
5 | Corridor | 3.02 | 31104 | 31105
| Logistic Room | 3.03 | 31107 | 31108
| Logistic Room | 3.04 | 31110 | 31111
| Classroom 2507 | 3.05 | 31113 | 31114
| Lecturer Room 5th Floor | 3.06 | 31116 | 31117
| Musholla | 3.07 | 31119 | 31120
| Faculty Room 5th Floor | 3.08 | 31122 | 31123
6 | Waiting Room Auditorium | 3.09 | 31125 | 31126
| Auditorium | 3.10 | 31128 | 31129
| Auditorium | 3.11 | 31131 | 31132
| Corridor 6th Floor | 3.12 | 31134 | 31135
| Meeting Room 6th Floor | 3.13 | 31137 | 31138
| Lecturer Room 6th Floor | 3.14 | 31140 | 31141
| Ciel Room | 3.15 | 31143 | 31144
| Visiting Prof. | 4.00 | 31146 | 31147
| Control Room Auditorium | 4.01 | 31149 | 31150